## Slide 1: Spill Prevention, Control, and Countermeasure (SPCC) Training

## Slide 2: SPCC Background Information
What is Spill Prevention, Control, and Countermeasure (SPCC)?
  Federal regulation required by EPA to prevent oil pollution in waters of the United States
  Oil Pollution Prevention Regulations
    40 CFR 112
    Originally published in 1973
Why is Texas State required to comply?
  We store more than 1,320 gallons of fuel or oil on campus in aboveground tanks
    Approximately 54,500 gallons onsite

## Slide 3: SPCC Background Information
What types of oils are covered in the SPCC Plan?
  Petroleum-based oils
    Crude oil, fuel, mineral oils, etc.
    New and used oils
  Animal-based oils
    Fats, oils, and greases from mammals or fish
  Vegetable oils
    Oils from seeds, nuts, fruits or kernels
SPCC regulation requires Texas State to:
  Prepare an SPCC Plan
    Annual employee training requirement
  Routinely inspect units and prevent discharge of oil storing units

## Slide 4: SPCC Background Information
Main Takeaway Points:
Why does Texas State need an SPCC Plan?
  To prevent accidental discharge of oil into navigable waters of the United States
  Illicit discharge of oil into San Marcos River or Sessom Creek can cause harm to wildlife, swimmers, and the ecosystem
Texas State can be subject to fines and violations if oil is discharged to local waterbodies

## Slide 5: Training Requirements
Applicable to all oil-handling employees of the University
Training is administered:
  Initially upon hire via SAP – online training database
  Annually thereafter
SPCC Training will cover:
  SPCC Plan background and program goals
  Potential spill pathways
  Prevention measures
  Response procedures

## Slide 6: Goals of SPCC Program
Spill Prevention
  Practices or procedures implemented to prevent oil discharges to the ground or navigable waters of the United States
Spill Control
  Control measures in place to prevent and/or contain incidental discharges of oil
Spill Countermeasures
  Procedures for responding to, cleaning up, and disposing of discharged oil
  Documentation and reporting

## Slide 7: Goals of SPCC Program
Spill Prevention Examples
  Maintain updated inventory of oil storage areas
  Maintain updated SPCC Plan
  Proper selection and installation of equipment
  Preventative maintenance
  Regular inspections of units
  Timely repair of malfunctioning systems
  Good oil-handling/fueling practices
  Employee training

## Slide 8: Goals of SPCC Program
Spill Control Examples
  Monitoring of leak detection systems
  Proper and timely reporting
  Utilizing secondary containment units
  Inspections of containment systems for functionality
  Spill kit utilization
Spill Countermeasure Examples
  Timely reporting to campus emergency response team (EHSRM)
  Swift response to spills
  Proper cleanup and disposal
  Documentation and reporting to the regulatory agency (if necessary)

## Slide 9: Spill Prevention

## Slide 10: Spill Prevention: Oil Storage
Where is oil stored on campus?
  Numerous elevator hydraulic systems
  Aboveground storage tanks – 6
  Oil-filled electrical step-down transformers – 86
  Electrical selector switch – 1
  Waste cooking oil tanks – 18
  Drum storage areas (used and new oil) – 9
    Diesel fueled generators – 24
    Hydraulic trash compactors – 9

## Slide 11: Oil Storage Locations
Cooking Oil
Grease Traps
Food Service Areas
  Dining Halls (Jones, Commons, The Den, The Lair, Harris)

## Slide 12: Oil Storage Locations
Vehicle Servicing Areas
  Maintenance Garages (Facilities, Parking Services)
  Fueling (Freeman Ranch)
Fuel Oil Storage
Lubricant Storage

## Slide 13: Oil Storage Locations
Vehicle Servicing Areas
  Maintenance Garages (Facilities, Parking Services)
Waste Oil
Used Oil, Oil Filters, and Antifreeze

## Slide 14: Oil Storage Locations
Various areas throughout campus with emergency power units or operational equipment
Transformers & Switches
Diesel Generators

## Slide 15: Inspection and Maintenance of Units
EHSRM Responsibilities:
  Conduct monthly inspections of all oil storage units
  Document findings and send reports to responsible departments
Responsible Department Duties:
  Complete preventative maintenance on units
  Respond to EHSRM reports and make necessary repairs
All Departments and Employees:
  Report unusual observations, leaks, or issues to supervisor
You are the eyes and ears of Texas State – We rely on you to report these issues so they can be fixed!

## Slide 16: Best Practices for Oil Handling
Oil Transfers/Deliveries
  Implement responsible transportation procedures to minimize spills/leaks
  Always pay close attention to box/transportation instructions (i.e. THIS SIDE UP)
  If using contractor, ensure they are experienced in transporting oil products
Vehicle and Equipment Maintenance
  Monitor fluid levels for volume decreases
  Inspect vehicles after performing maintenance to ensure all lines are disconnected and valves are closed

## Slide 17: Spill Prevention
What if we don’t implement these prevention procedures?
  Failure to prevent oil discharges can result in oil entering “navigable waters of the United States” via:
    Spillage on the ground uphill from a storm drain
    Intentional dumping of oil directly into a storm drain or waterbody (San Marcos River, Sessom Creek, etc.)
Storm drain inlet receiving rainwater

## Slide 18: Spill Prevention
What if we don’t implement these prevention procedures?
  If oil enters “navigable waters of the United States,” the following can occur:
    Detrimental environmental impacts to wildlife, swimmers, and habitat
    Texas State may be subject to federal/state violations (and potential fines)
Oil that has entered navigable waters of the U.S. is considered an illicit discharge. Illicit discharges are prohibited by UPPS 04.05.16 and should be reported immediately.

## Slide 19: Spill Control

## Slide 20: Spill Control
Methods of Spill Control
  Utilization of leak detection systems
    Secondary containment is used to capture oil that is accidentally discharged from unit
  Double Walled Transfer Piping
    Preventing leakage and backup to piping with “pipe over pipe” protection
  Slug Control Plan
    Local Program required document detailing how to prevent spills

## Slide 21: Spill Control
Double Walled Piping

## Slide 22: Spill Control
Methods of Spill Control
  Utilize secondary containment units (permanent or temporary)
    Secondary containment is used to capture oil that is accidentally discharged from unit
  Inspect secondary containment for cracks, openings, or weaknesses that could result in a discharge of oil to the ground
  Monitor spills in secondary containment, clean as needed

## Slide 23: Spill Control
Methods of Spill Control
  Double-walled tanks do not require structural secondary containment outside the unit
    Secondary wall acts as secondary containment within the unit to capture discharges of oil
Double Walled Tank

## Slide 24: Spill Control
Methods of Spill Control
  Reporting discharges to EHSRM as soon as possible can help control the impacts of the spill
  If discharges are not reported on time…
    Texas State could be liable for impacts to the environment
    Regulatory reporting will be delayed, resulting in possible violations and fines
    Impacts to wildlife could be exacerbated should a response be delayed
EHSRM Phone – Regular Business Hours
512-245-3616
EHSRM Phone – After Hours/On-Call
512-738-6650

## Slide 25: Spill Countermeasure

## Slide 26: Spill Response
Reporting and Responding to Spills
  Safety First
    Call 911 immediately if anyone is injured
    Extinguish open flames or ignition sources (ex: cigarettes)
  Stop the Spill
    If possible and safe to do, stop the spill at it’s source
      Turn off valves
      Make sure containers are upright
      Protect floor drains/storm inlets
Notify EHSRM
Regular Business Hours: 512-245-3616
After Hours: 512-738-6650

## Slide 27: Spill Response
Incidental or “Small” Spills
  Less than or equal to five (5) gallons
  Considered “manageable”
  Low threat to the environment (i.e. not discharged to sanitary or storm sewer, isolated in nature)
Clean-Up Procedures
  Only begin clean-up activities if you have appropriate training, if supplies are readily available, AND only if you feel comfortable cleaning up the spill
  Use appropriate PPE and spill response supplies (clean-up supplies will depend on the spill)
  Contact EHSRM for disposal of materials
If you do not have spill response supplies, or you do not feel comfortable cleaning up the spill –
Contact EHSRM for assistance

## Slide 28: Spill Response
Examples of Incidental Spills

## Slide 29: Spill Response
Emergency or “Large” Spills
  More than five (5) gallons
  Imminent threat to the environment
  Considered outside the scope of Texas State Spill Response Team
  Notify EHSRM immediately
Clean-Up Procedures
  EHSRM will contact 911 or spill response contractor
  You may be required to provide additional information for reporting (i.e. who, what, when, where, how)

## Slide 30: Spill Response
When in doubt – Call EHSRM
Regular Business Hours: 512-245-3616
After Hours: 512-738-6650
Contact EHSRM if…
  The spill is more than five gallons and/or unmanageable
  You need assistance with spill cleanup
  You are unsure about proper spill cleanup methods
  The spill has discharged to storm or sanitary sewer

## Slide 31: Spill Kits
Where are spill kits located?
  Strategically placed throughout campus
What is inside your spill kit?
  Baking soda
  Absorbent pads
  Gloves
  Goggles
  Booms
  Trash Bags
  Waste tags
  Emergency Numbers
Notify your supervisor if EHSRM needs to restock materials

## Slide 32: Spill Kits

## Slide 33: Spill Kit Locations

## Slide 34: Spill Kits
Strategically Placed
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location
Spill Kit Location

## Slide 35: Reporting Spills
Reportable Quantities
  What is considered “reportable” to the State of Texas (TCEQ) or EPA?
  Any petroleum product (oil, gas, kerosene, diesel, etc.) that makes a sheen on navigable waters (San Marcos River, Sessom Creek)
  Chemicals discharged into water or onto land that exceeds the Reportable Quantity limit
EHSRM will contact the appropriate regulatory entity in the event of a discharge to land or navigable waters –
This is only for your information

## Slide 36: Main Points
Be aware of where oil and chemicals are stored
Preventing spills is easier and cheaper than cleanup measures
All storm drains lead to the San Marcos River
If you see a spill or leak, report it immediately to your supervisor
Cleanup any spills in your workspace as soon as possible
Contact EHSRM with any questions – We are here to help!

## Slide 37: Questions/Comments?
Environmental Health, Safety and Risk Management Department
Smith House
736 Oscar Smith St., San Marcos, TX 78666
http://www.fss.txstate.edu/ehsrm/
EHSRM Contact Info
Regular Business Hours: 512-245-3616
After Hours: 512-738-6650